## PhysicalDiagram
1
9
11
8
20
2
3
4
5
7
10
12
13
14
16
21
23
1
2
3
4
5
6
7
8
9
11
10
17
18
19
20
21
22
15
6

## Validate
Flows | Processes | Wastes
RESOURCE | PRODUCTIVE | DEFAULT
INTERNAL | DISSIPATIVE | MANUAL
OUTPUT |  | RESOURCES
WASTE |  | EXERGY
COST
IRREVERSIBILITY
HYBRID

## Flows
key | type
B1 | INTERNAL
B2 | INTERNAL
B3 | INTERNAL
B4 | INTERNAL
B5 | INTERNAL
B6 | INTERNAL
B7 | INTERNAL
B8 | INTERNAL
B9 | INTERNAL
B10 | INTERNAL
B11 | INTERNAL
B12 | INTERNAL
B13 | INTERNAL
B14 | INTERNAL
GN | RESOURCE
WTA1 | INTERNAL
WTA2 | INTERNAL
WTB1 | INTERNAL
WTB2 | INTERNAL
WP1 | INTERNAL
WP2 | INTERNAL
WN | OUTPUT
QC | WASTE

## Processes
key | description | fuel | product | type
CALD | Caldera | GN | (B1-B11)+(B4-B3) | PRODUCTIVE
TVA1 | Turbina Alta 1 | B1-B2-B12 | WTA1 | PRODUCTIVE
TVA2 | Turbina Alta 2 | B2-B3 | WTA2 | PRODUCTIVE
TVB1 | Turbina Baja 1 | B4-B5-B14 | WTB1 | PRODUCTIVE
TVB2 | Turbina Baja 2 | B5-B6 | WTB2 | PRODUCTIVE
DESG | Desgasificador | B8+B13+B14 | B9 | PRODUCTIVE
PHTR | Precalentador | B12-B13 | B11-B10 | PRODUCTIVE
PMP1 | Bomba 1 | WP1 | B8-B7 | PRODUCTIVE
PMP2 | Bomba 2 | WP2 | B10-B9 | PRODUCTIVE
ALTR | Alternador | WTA1+WTA2+WTB1+WTB2 | WN+WP1+WP2 | PRODUCTIVE
COND | Condensador | B6-B7 | QC | DISSIPATIVE

## Exergy
key | Reference | ETV89 | ALT97 | CND8 | T490
B1 | 119669 | 120857 | 120916 | 121830 | 119366
B2 | 72941 | 73841 | 73701 | 74258 | 72842
B3 | 62368 | 63159 | 63018 | 63494 | 62376
B4 | 81615 | 82454 | 82466 | 83089 | 82209
B5 | 54430 | 55082 | 54997 | 55834 | 54836
B6 | 7492 | 7599 | 7570 | 10159 | 7548
B7 | 105.4 | 106.5 | 106.5 | 193.9 | 106.2
B8 | 130.1 | 131.5 | 131.5 | 219.3 | 131.1
B9 | 7205 | 7276 | 7280 | 7335 | 7268
B10 | 8158 | 8239 | 8243 | 8305 | 8238
B11 | 16346 | 16508 | 16516 | 16641 | 16495
B12 | 11581 | 11695 | 11702 | 11790 | 11684
B13 | 2207 | 2224 | 2230 | 2247 | 2246
B14 | 8580 | 8677 | 8669 | 8315 | 8632
GN | 286333 | 288733 | 289318 | 291505 | 287575
WTA1 | 33159 | 33116 | 33505 | 33758 | 32843
WTA2 | 9893 | 9926 | 9996 | 10071 | 9784
WTB1 | 17639 | 17622 | 17823 | 17958 | 17767
WTB2 | 42466 | 42504 | 42909 | 41391 | 42784
WP1 | 28.84 | 29.14 | 29.14 | 29.49 | 29.05
WP2 | 1065 | 1076 | 1076 | 1084 | 1085
WN | 100000 | 100000 | 100000 | 100000 | 100000
QC | 7386.6 | 7492.5 | 7463.5 | 9965.1 | 7441.8

## Format
key | width | precision | unit
EXERGY | 11 | 1 | (kW)
EXERGY_COST | 11 | 1 | (kW)
EXERGY_UNIT_COST | 10 | 4 | (J/J)
GENERALIZED_COST | 10 | 1 | (kW)
GENERALIZED_UNIT_COST | 10 | 4 | (J/J)
DIAGNOSIS | 11 | 2 | (kW)

## WasteDefinition
key | type | recycle
QC | RESOURCES | 0